## Ark1
|  |  | Eta-0 | a1 | a2 | Tm | Ta | G
| Eta | 52.25% | 0.857 | 3.08 | 0.013 | 57.5 | 20 | 400 | W/m2 Avg. | Cph
[5 empty] | Tf | 75 |  | 540 | W/m2 Avg. | Odessa
[5 empty] | Tr | 40 |  | 448.8 | W/m2 Avg. | Kyiv
| Kiev | Temp | Eff | Output |  | Odessa | Temp | Eff |  |  | Copenhagen |  |  |  |  | Kyiv |  | Odessa
Jan | 37 | -2 | 34.61% | 12.8064 |  | 47 | 2 | 46.63% | 21.9156 |  | 30 | 3 | 34.08% | 10.2245 | Jan | 12.038 | Jan | 20.6007
Feb | 53 | 0 | 36.66% | 19.431 |  | 66 | 4 | 48.29% | 31.8744 |  | 45 | 3 | 34.08% | 15.3368 | Feb | 18.2652 | Feb | 29.962
Mar | 92 | 6 | 42.67% | 39.2604 |  | 97 | 6 | 49.94% | 48.4427 |  | 90 | 6 | 37.43% | 33.6827 | Mar | 36.9048 | Mar | 45.5361
Apr | 117 | 15 | 51.3% | 60.0226 |  | 129 | 15 | 57.11% | 73.673 |  | 130 | 11 | 42.87% | 55.728 | Apr | 56.4212 | Apr | 69.2527
May | 146 | 21 | 56.79% | 82.9163 |  | 165 | 21 | 61.67% | 101.7625 |  | 157 | 16 | 48.15% | 75.5919 | May | 77.9413 | May | 95.6567
June | 153 | 25 | 60.34% | 92.3149 |  | 170 | 25 | 64.62% | 109.8542 |  | 150 | 19 | 51.24% | 76.8565 | June | 86.776 | June | 103.263
July | 147 | 27 | 62.07% | 91.2489 |  | 178 | 27 | 66.06% | 117.5943 |  | 146 | 22 | 54.27% | 79.233 | July | 85.7739 | July | 110.5386
Aug | 140 | 27 | 62.07% | 86.9037 |  | 172 | 27 | 66.06% | 113.6304 |  | 124 | 21 | 53.27% | 66.0488 | Aug | 81.6895 | Aug | 106.8126
Sep | 104 | 21 | 56.79% | 59.0636 |  | 129 | 21 | 61.67% | 79.5597 |  | 90 | 17 | 49.18% | 44.2658 | Sep | 55.5198 | Sep | 74.7862
Oct | 73 | 13 | 49.42% | 36.0801 |  | 96 | 13 | 55.55% | 53.3292 |  | 56 | 12 | 43.94% | 24.6045 | Oct | 33.9153 | Oct | 50.1294
Nov | 30 | 8 | 44.63% | 13.3896 |  | 47 | 10 | 53.18% | 24.9926 |  | 29 | 7 | 38.53% | 11.1727 | Nov | 12.5862 | Nov | 23.493
Dec | 28 | 1 | 37.68% | 10.5501 |  | 44 | 4 | 48.29% | 21.2496 |  | 20 | 4 | 35.2% | 7.0405 | Dec | 9.9171 | Dec | 19.9746
SUM |  |  |  | 603.9874 |  |  |  |  | 797.8783 |  |  |  |  | 499.7858 |  | 567.7482 |  | 750.0056
Reduction parameter |  |  |  | 0.94 |  |  |  |  | 0.94 |  |  |  |  | 0.94
Heat/m2 |  |  |  | 567.7482 | kWh/m2 |  |  |  | 750.0056 | kWh/m2 |  |  | 471 | 469.7986 | kWh/m2
Area |  |  |  | 10000 | m2 |  |  |  | 10000 | m2 |  |  |  | 10000 | m2
Total |  |  |  | 5677.4818 | MWh |  |  |  | 7500.0562 | MWh |  |  |  | 4697.9862 | MWh
Costs
Plant excluding day-night storage |  |  | 250000 | 167 | €/m2
Day-nigth storage |  |  | 60 | €/m3 | 12 | $/m2 solar panel
Solar panels |  |  | 10000 | m2 | Tank | 2000 | m3
Plant excluding day-night storage |  |  | 1920000 | €
Storage tank |  |  | 120000 | $
Investment cost |  |  | 2040000 | €
Fixed O&M | 0.04 | €/m2 | 400 | €/year
Electricity use | 3.1068 | kWh/MWh_h | 881.9438 | €/y at electricity price |  | 50 | €/MWh = | 2000 | UAH/MWh
Pay-back | 5% | interest | 132704.9276 | €/year, lifetime |  | 30 | years
Annual costs |  |  | 133986.8713 | €/year
Yield, Kyiv |  |  | 5677.4818 | MWh/year
Heat price Kyiv |  |  | 0.023444 | €/kWh = |  |  |  | 937.7744 | UAH/MWh
Yield, Odessa |  |  | 7500.0562 | MWh/year
Solar heat price Odessa |  |  | 0.017747 | €/kWh |  |  |  | 709.8876 | UAH/MWh
Plant excluding day-night storage |  |  | 250000 | 167 | €/m2
Day-night storage |  |  | 60 | €/m3 | 12 | $/m2 solar panel
Solar panel |  |  | 40000 | m2 | Tank | 8000 | m2
Investment cost |  |  | 6930000 | €
O&M | 0.04 | €/m2 | 1600 | €
Depreciatio | 15 | year | 462000 | €
Yield Kyiv |  |  | 22709.9273 | MWh
Solar heat price, Kyiv |  |  | 0.020414 | €/kWh | 87.07%